## Inputs
Rev 1, 10 Jul 2015
Inputs - Please provide values in the highlighted cells
Parameter | Value |  | Converted value | Help
Temperature (T) - °C | 25 | °C |  | Please enter the normal temperature of the area
Present humidity (RH%) | 70 | % | 16.1135 | Please enter maximum level of present humidity
Humidity to be achieved (RH%) | 40 | % | 9.2077 | Please enter the humidity you want to achieve
Room volume in cubic meter | 180 | m3 |  | Calculate the volume by multiplying Length x Width x Height in meters
Air exchange ratio | 1 |  |  | This is ratio of air inflow and outflow. The ratio is generally 1. If you are not sure, leave it as 1
Results
Dehumidification capacity | 1.243 | kg/hr or liter / hour
| 29.833 | kg/hr or liter / day
Method of Calculation
Absoulte humidity level is calculated in g/m3 for both present humidity level and absolute humidity level
Thereafter difference of the same is calculated.
From this value and the size of the room, dehumidification capacity is calculated

## RH1 (hidden)
[7 empty] | A | m | Tn | T
Present temperature T |  | 25 |  |  |  |  | 6.1164 | 7.5914 | 240.7263 | 20
Present humidity RH1 |  | 70
Desired humidity RH2 |  | 40
Size of Room | [6 empty] | mxT | 151.8277
| Length (m) | [5 empty] | T+tn | 260.7263
Width (m)
| Height (m) | [5 empty] | mxT | 0.58233
or | [6 empty] | T+tn
Volume of the room (m3)
3.8223
Step 1 : Calculate Saturation Vapour Pressure Pws | [5 empty] | Note(Prakash) |  | 23.3789
|  |  | A | m | Tn |  |  | 18.7032
If temperature between -20to+50°C |  |  | 6.1164 | 7.5914 | 240.7263 | equal 50 or not
If temperature between +50°Cto+100°C |  |  | 6.0049 | 7.3379 | 229.3975 | equal 50 or not |  | 13.8243
Pws=A x 10^(mxT)/(T+Tn) hPa
First calculate Pws at T
| m x T | = | 189.7846
| T+Tn | = | 265.7263
| (mxT)/(T+Tn) | = | 0.71421
| 10^(mxT)/(T+Tn) | = | 5.1786
Pws= | A x 10^(mxT)/(T+Tn) | = | 31.6745
Step 2 : Calculate vapour pressure Pw in hPa
Pw=Pws x RH1 /100
| Pws | = | 31.6745
| RH1 | = | 70
| Pw | = | 22.1722
Step 3 : Calculate Absolute humidity (Ag) in g/m3
Ag = (2.16679 x Pw x 100) / (273.15+T)
| Pw | = | 22.1722
| 2.16679 x Pw x 100 | = | 4804.2397
| (273.15+T) | = | 298.15
| Ag1 | = | 16.1135

## RH2 (hidden)
Present temperature T |  | 25 |  |  |  | A | m | Tn | T
Present humidity RH1 |  | 70 |  |  |  | 6.1164 | 7.5914 | 240.7263 | 20
Desired humidity RH2 |  | 40
Size of Room
| Length (m) |  |  |  |  | mxT | 151.8277
| Width (m) |  |  |  |  | T+tn | 260.7263
Height (m)
or | [5 empty] | mxT | 0.58233
Volume of the room (m3) | [5 empty] | T+tn
Step 1 : Calculate Saturation Vapour Pressure Pws | [6 empty] | 3.8223
|  |  | A | m | Tn |  | 23.3789
If temperature between -20to+50°C |  |  | 6.1164 | 7.5914 | 240.7263 |  | 18.7032
If temperature between +50°Cto+100°C |  |  | 6.0049 | 7.3379 | 229.3975
13.8243
Pws=A x 10^(mxT)/(T+Tn) hPa
First calculate Pws at T
| m x T | = | 189.7846
| T+Tn | = | 265.7263
| (mxT)/(T+Tn) | = | 0.71421
| 10^(mxT)/(T+Tn) | = | 5.1786
Pws= | A x 10^(mxT)/(T+Tn) | = | 31.6745
Step 2 : Calculate vapour pressure Pw in hPa
Pw=Pws x RH1 /100
| Pws | = | 31.6745
| RH2 | = | 40
| Pw | = | 12.6698
Step 3 : Calculate Absolute humidity (Ag) in g/m3
Ag = (2.16679 x Pw x 100) / (273.15+T)
| Pw | = | 12.6698
| 2.16679 x Pw x 100 | = | 2745.2798
| (273.15+T) | = | 298.15
| Ag2 | = | 9.2077

## dehumidification (hidden)
Ag1-Ag2
Ag1 | 16.1135
Ag2 | 9.2077
Ag1-Ag2 | 6.9058
Volume | 180
Air exchange rate | 1
| 1243.0413 |  | Dehumidification capacity | g/hr
| 1.243 |  |  | kg/hr
| 29.833 |  |  | kg/day
| 1.243 | ltr/hr | Dehumidification capacity | ltr/hr
| 29.833 | ltr/day | Dehumidification capacity | ltr/day